## UQ
Category | Class | Parameter | On/Off | Probability distribution
|  |  |  | Distribution type | Mean or Mode | Std Dev. | min | max
Building envelop | StandardOpaqueMaterial | Conductivity | Off | Normal Relative | 1 | 5% | 0 | NA
| StandardOpaqueMaterial | Density | Off | Normal Relative | 1 | 1% | 0 | NA
| StandardOpaqueMaterial | SpecificHeat | Off | Normal Relative | 1 | 12.5% | 0 | NA
| StandardOpaqueMaterial | SolarAbsorptance | Off | Normal Relative | 1 | 7% | 0 | 1
| StandardOpaqueMaterial | ThermalAbsorptance | Off | Normal Relative | 1 | 2% | 0 | 1
| StandardOpaqueMaterial | VisibleAbsorptance | Off | Normal Relative | 1 | 7% | 0 | 1
| StandardGlazing | Conductivity | Off | Normal Relative | 1 | 5% | 0 | NA
| StandardGlazing | ThermalResistance | Off | Normal Relative | 1 | 5% | 0 | NA
| StandardGlazing | SolarTransmittance | Off | Normal Relative | 1 | 1% | 0 | NA
| StandardGlazing | FrontSideSolarReflectance | Off | Normal Relative | 1 | 1% | 0 | NA
| StandardGlazing | BackSideSolarReflectance | Off | Normal Relative | 1 | 1% | 0 | NA
| StandardGlazing | VisibleTransmittance | Off | Normal Relative | 1 | 1% | 0 | NA
| StandardGlazing | FrontSideVisibleReflectance | Off | Normal Relative | 1 | 1% | 0 | NA
| StandardGlazing | BackSideVisibleReflectance | Off | Normal Relative | 1 | 1% | 0 | NA
| StandardGlazing | InfraredTransmittance | Off | Normal Relative | 1 | 1% | 0 | NA
| StandardGlazing | FrontSideInfraredHemisphericalEmissivity | Off | Normal Relative | 1 | 1% | 0 | NA
| StandardGlazing | BackSideInfraredHemisphericalEmissivity | Off | Normal Relative | 1 | 1% | 0 | NA
| StandardGlazing | DirtCorrectionFactor | Off | Normal Relative | 1 | 10% | 0 | NA
| Infiltration | FlowPerExteriorArea | On | Triangle Absolute | 0.00095 |  | 0.00031944 | 0.0028944
Operation | Lights | WattsPerSpaceFloorAreax | On | Normal Relative | 1 | 50% | 0 | 50
| PlugLoad | WattsPerSpaceFloorArea | On | Normal Relative | 1 | 50% | 0 | 50
| People | SpaceFloorAreaPerPerson | On | Normal Relative | 1 | 50% | 0 | 30
HVAC | HotWaterBoiler | Efficiency | Off | Normal Relative | 1 | 1% | 0 | 1
| SteamBoiler | Efficiency | Off | Normal Relative | 1 | 1% | 0 | 1
| FanVariableVolume | Efficiency | Off | Normal Relative | 1 | 1% | 0 | 1
| FanVariableVolume | Motor_efficiency | Off | Normal Relative | 1 | 1% | 0 | 1
| FanConstantVolume | Efficiency | Off | Normal Relative | 1 | 1% | 0 | 1
| FanConstantVolume | Motor_efficiency | Off | Normal Relative | 1 | 1% | 0 | 1
| PumpVariableSpeed | Motor_efficiency | Off | Normal Relative | 1 | 1% | 0 | 1
| PumpConstantSpeed | Motor_efficiency | Off | Normal Relative | 1 | 1% | 0 | 1
| DesignSpecificationOutdoorAir | OutdoorAirFlowPerPerson | Off | Normal Relative | 1 | 1% | 0 | NA
| DesignSpecificationOutdoorAir | OutdoorairFlowPerZoneFloorArea | On | Normal Relative | 1 | 1% | 0 | NA
| DesignSpecificationOutdoorAir | OutdoorAirFlowRate | Off | Normal Relative | 1 | 1% | 0 | NA
| SingleSpeedDXCoolingUnits | RatedTotalCoolingCapacity | Off | Normal Relative | 1 | 1% | 0 | NA
| SingleSpeedDXCoolingUnits | RatedSenisbleHeatRatio | Off | Normal Relative | 1 | 1% | 0.5 | 1
| SingleSpeedDXCoolingUnits | RatedCOP | Off | Normal Relative | 1 | 1% | 0 | NA
| SingleSpeedDXCoolingUnits | RatedAirFlowRate | Off | Normal Relative | 1 | 1% | 0 | NA
| TwoSpeedDXCoolingUnits | RatedHighSpeedCOP | Off | Normal Relative | 1 | 1% | 0 | NA
| TwoSpeedDXCoolingUnits | RatedLowSpeedCOP | Off | Normal Relative | 1 | 1% | 0 | NA
| ChillerElectricEIR | ReferenceCOP | Off | Normal Relative | 1 | 1% | 0 | NA
Zone Control | ThermostatSettings | ThermostatSetpointHeating | Off | Uniform Absolute | 0 | 0 | 0.2 | 0.5
| ThermostatSettings | ThermostatSetpointCooling | Off | Uniform Absolute | 0 | 0 | 0.2 | 0.5

## CellList (hidden)
On | Normal Relative
Off | Normal Absolute
Uniform Relative
Uniform Absolute
Triangle Absolute
Triangle Relative
LogNormal Absolute

## References (hidden)
References
Abushakra, B, A Sreshthaputra, JS Haberl, and DE Claridge. 2001. Compilation of diversity factors and schedules for energy and cooling load calculations, Final Report of the ASHRAE Research Project 1093-RP. Energy Systems Laboratory, Texas A&M University.
ASHRAE (2009). ASHRAE Handbook – Fundamentals. ASHRAE Inc., Atlanta, GA.
ASHRAE (2011). ASHRAE Handbook – HVAC Applications. ASHRAE Inc., Atlanta, GA.
ASHRAE Standard 55 (2004). Thermal environmental conditions for human occupancy. ASHRAE Inc., Atlanta, GA.
BSRIA (2003). Rules of thumb – Guidelines for building services. Building Services Research and Information Association, Bracknell, UK.
CIBSE (2004). Guide G: Public Health Engineering. Charted Institution of Building Services Engineers, London, UK.
De Wit, S., and Augenbroe, G. (2002). Analysis of uncertainty in building design evaluations and its implications. Energy and Buildings, 34: 951-958.
Emmerich, S.J., McDowell, T., and Anis, W. (2005). Investigation of the impact of commercial building envelope airtightness on HVAC energy use. Report NISTIR 7238, National Institute of Standards and Technology.
Favarolo, P. A. and H. Manz (2005). Temperature-driven single-sided ventilation through a large rectangular opening. Building and Environment 40(5): 689-699.
Goldner, F.S. (1994). Energy use and domestic hot water consumption. Final Report Phase 1, Energy Management & Research Associates.
Goldner, F.S. (1994). Energy use and domestic hot water consumption. Final Report Phase 1, Energy Management & Research Associates.
Khazii, J. (2012). Effects of sub-optimal component performance on overall cooling system energy consumption and efficiency. Ph.D. Dissertation. Georgia Institute of Technology, Atlanta.
Macdonald, I.A. (2002). Quantifying the effects of uncertainty in building simulation. Ph. D. Dissertation, University of Strathclyde, Glasgow, Scotland, UK.
Persily A.K., and Gorfain, J. (2004). Analysis of ventilation data from the U.S. Environmental Protection Agency building assessment survey and evaluation (BASE) study. Report NISTIR 7145, National Institute of Standards and Technology.
Persily A.K., and Gorfain, J. (2004). Analysis of ventilation data from the U.S. Environmental Protection Agency building assessment survey and evaluation (BASE) study. Report NISTIR 7145, National Institute of Standards and Technology.
Persily, A.K. (1998). Airtighness of commercial and institutional buildings: blowing holes in the myth of tight buildings. Proceedings of Thermal Performance of the Exterior Envelopes of Buildings, 829-837.
Persily, A.K. (1999). Myths about building envelopes. ASHRAE Journal, March, 39-45.
Sun, Y. (2014). Closing the building energy performance gap by improving our predictions. Ph.D. Dissertation, Georgia Institute of Technology, Atlanta.
Sun, Y., Heo, Y., Tan, M., Xie, H., Wu, C. F. J. and Augenbroe, G. (2014). Uncertainty Quantification of Microclimate Variables in Building Energy Models. Journal of Building Performance Simulation. 7(1), 17-32.
Wang, B., D. W. Etheridge, et al. (2011). Wind tunnel investigation of natural ventilation through multiple stacks. Part 1: Mean values. Building and Environment 46(7): 1380-1392.
Wang, Q., Augenbroe, G. and Sun, Y. (2014). The Role of Construction Detailing and Workmanship in Achieving Energy Efficient Buildings. Construction Research Congress 2014, Atlanta, Georgia.
Yan, B., and Malkawi, A.M. (2012). Uncertainties in HVAC system operations. Internal Report. T.C. Chan Center for Building Simulation and Energy Studies, University of Pennsylvania.