## Slide 1: BCUS101 – Sensitivity Analysis Tutorial
A Integrated Workflow to Perform BCUS
Bayesian Calibration, Uncertainty Analysis and Sensitivity Analysis
on OpenStudio Models
September 2019

## Slide 2: Read me
Limited number of output variables:
  Electricity:Facility
  Electricity:Building
  Gas:Facility
  Heating:Gas
  Heating:Electricity
  Cooling: Electricity
  Electricity:HVAC
Limited subset of uncertain parameters
Check the “Parameter_UQ_Repository_V1.0.xlsx” for list of uncertain variables
Sensitivity analysis only do one year of simulation

## Slide 3: Overview
This tutorial will lead you through the procedures of applying BCUS - Bayesian Calibration, Uncertainty Analysis and Sensitivity Analysis on OpenStudio models.
Before you start, a functioning OpenStudio model and an EPW weather file are desired to illustrate the building and its surrounding environment being analyzed. Details of how to build an OpenStudio building model can be found here. Weather files can be downloaded here.

## Slide 4: Get Started
PREREQUISITE
INSTALLATIONS
Executing BCUS typically requires the following tools and packages:
OpenStudio
EnergyPlus
Microsoft Office(Some functions will be eliminated if using Libre Office in Ubuntu, i.e. drop down list)
R
R packages
SET ENVIRONMENT
Once the prerequisite tools are installed, set up the platform variables to access executables, examples and tests.
TEST INSTALLATION
To make sure BCUS runs correctly:
Test the Ruby-OpenStudio environment
Test installation by running a simple example
SIMPLE
EXAMPLES
Step by step following the tutorial which demonstrate the basic procedure of running BCUS.
Notes: - To use Ruby from OpenStudio Installation Package: Add path environmental variable: e.g., C:\Program Files\openstudio-2.7.0\ruby-install\ruby\bin
Install Ruby gems: run cmd.exe as administrator, then install required gems like e.g. “gem install rinruby”

## Slide 5: Example File
Building Description
In the Example folder, users can find the ExampleBuilding.osm model with required input files in order to run BCUS.
The example building is a 3-story, 100,000 sqft office building located in PA. It has a rectangular footprint and 50% window-to-wall ratio. The heating, ventilation and air conditioning system in the building is VAV system with DX cooling (COP =2.6). The electric resistance serves the central heating and reheat in the VAV system.

## Slide 6: Examples
Create a Project Folder
The BCUS Package is distributed in the format of a zip folder named “BCUS.zip", the first step is to extract the folder to a local directory on your computer. The main folder contains 4 subfolders as shown below.
BCUSCode: Ruby codes to run the program
Install: Help first time users install the required packages, setup
the path and check the status of the installation
Example: The example building model and required inputs
Tutorials: Tutorial document

## Slide 7: Examples: Input Files Format
Input Files
Create a project folder inside the main folder
Copy the following files from ”…\BCUS\Example” and paste them to the project folder. Now you would see the following files in your project folder.
After pasting the five required input files for uncertainty analysis, replace the ExampleBuilding.osm with your building model; replace the .epw file with the weather file for your building’s location.

## Slide 8: Step 1: Edit Executable Bash/Batch Script
Open Sensitivity_Analysis.bat file using any available text editing software:
Replace current file names with your building model name and weather file name.
You can save the modified bash script with a new name, such as Run_SA.bat or just keep the old name.
Replace with the name of your
building model
Replace with the weather file of your building model
List of inputs. Add --help for detail explanations
Will use default values if left blank in the input

## Slide 9: About the Bash Script
--osm: The name of the OpenStudio model (.osm)
--epw: The name of the weather file(.epw)
--uqRepo: The name of the UQ parameter repository in the directory
--outFile: The name of the simulation output setting file (.csv)
--morrisR: The number of repetitions for the Morris method
--morrisL: The number of levels for the Morris method
--seed: Need to be an integer. If same, the sequence of the samples will be the same
--numProcesses: The number of parallel processes for running EnergyPlus simulations
--noEP: If true, no EnergyPlus simulation will be performed
--noCleanup: If true, intermediate files will be kept
--interactive: If true, there will be dialogue between the user and the program
--verbose: If true, run in verbose mode with more output info printed
--help: Display help

## Slide 10: Step 2: Check the parameter UQ-Repository
Turn on the parameters which you want to investigate in the uncertainty analysis in the Parameter_UQ_Repository_V1.0.xlsx file.
Leave the other setting as default unless you have the confidence in the knowledge you have on a specific parameter.
Default probability distribution value
Turn on/off sources
of uncertainty

## Slide 11: Step 3: Outputs and Report Frequency Settings
Use Simulation_Output_Settings.xlsx to setup simulation outputs:
    Navigate to the TotalEnergy tab to add total energy output variables using the dropdown list
    Navigate to the Meters tab to add meters and report frequency using the dropdown list
    .

## Slide 12: Step 4: Run Executable Bash Script in the Terminal
Launch the Terminal in your operating system:
For OSX – Press Command + Space and type terminal and press Enter
For Linux – Open the Dash by clicking the Ubuntu icon in the upper-left, type terminal, and
select the Terminal application from the results that appear.
or simply hit the keyboard shortcut Ctrl-Alt+T.
For Windows – Click Start, in the search box type cmd and press Enter
Navigate to your project folder
Click the cursor in your Terminal/cmd type:
cd <your project folder directory>
For example,
  cd /Users/username/Documents/OpenStudio/BCUS/Example
Run the bash script you just modified by type:
Sensitivity_Analysis.bat (Windows)
sh Run_SA.sh (Linux/OSX)

## Slide 13: Step 5:Generate Distributions of Uncertain Parameters
The first step of the sensitivity analysis is to generate a distribution table of uncertain parameters, which you can find it at ../SA_Output/UQ_building_name.csv
The example building model includes five parameters in the sensitivity analysis:
infiltration rate, lighting load, plug load, occupancy load, and design outdoor air flow rate.
Parameter Type | Object in the model | Parameter Base Value | Distribution | Mean or Mode | Std Dev | Min | Max
Infiltration | FlowPerExteriorArea |  | Triangle Absolute | 0.00095 |  | 0.000319 | 0.002894
Lights_WattsPerSpaceFloorArea | Office_Space_Type | 15.17433543 | Normal Relative | 1 | 0.5 | 0 | 50
PlugLoad_WattsPerSpaceFloorArea | Office_Space_Type | 8.072932813 | Normal Relative | 1 | 0.5 | 0 | 50
People_SpaceFloorAreaPerPerson | Office_Space_Type | 18.58060872 | Normal Relative | 1 | 0.5 | 0 | 30
DesignSpecificOutdoorAirFlowPerZoneFloorArea | Office_Outdoor_Air | 0.0004318 | Normal Relative | 1 | 0.01 | 0 | NA

## Slide 14: Design Matrix and Simulation Runs
In the second step, the program will generate a design matrix based on the Morris method (Morris 1991). The design matrix contains the value of parameters generated from distributions specified in the UQ table.
In the third step, the program runs certain number of OpenStudio models which have been generated based on the design matrix.
Morris, M. D. (1991). Factorial sampling plans for preliminary computational experiments. Technometrics, 33(2), 161-174.

## Slide 15: Check SA Results
After simulations have completed, the user can find the output in the SA_Output folder. Ranking of parameters is based on mu.star.
SA on Total Electricity Use
SA on Total Gas Use
 | mu | mu.star | sigma
Infiltration: FlowPerExteriorArea | -389.818 | 932.3372 | 1395.541
Lights_WattsPerSpaceFloorArea: Office_Space_Type | -1216.62 | 1216.616 | 817.0287
PlugLoad_WattsPerSpaceFloorArea: Office_Space_Type | -430.791 | 1829.638 | 2739.633
People_SpaceFloorAreaPerPerson: Office_Space_Type | -102.665 | 589.2675 | 960.778
DesignSpecificOutdoorAirFlowPerZoneFloorArea: Office_Outdoor | -735.549 | 1405.033 | 1493.021
 | mu | mu.star | sigma
Infiltration: FlowPerExteriorArea | -0.05227 | 0.0784 | 0.115853
Lights_WattsPerSpaceFloorArea: Office_Space_Type | 0.021778 | 0.108889 | 0.141974
PlugLoad_WattsPerSpaceFloorArea: Office_Space_Type | 0.113244 | 0.296178 | 0.351629
People_SpaceFloorAreaPerPerson: Office_Space_Type | 0.113244 | 0.121956 | 0.125482
DesignSpecificOutdoorAirFlowPerZoneFloorArea: Office_Outdoor | -0.06098 | 0.148089 | 0.185047

## Slide 16: Check SA Results in Output Folders
A Sensitivity_Plots.pdf file will be saved to ../SA_Output. Raw results from simulations are saved to ../SA_Simulations. Open the pdf file and check the plot of the sensitivity analysis.
Note:
The lower ranked parameters in the sensitivity analysis result are not stable upon repetitive runs of the same input settings, that is, parameters near the origin in a sensitivity plot would fluctuate upon each runs.
The parameter near the origin in the sensitivity plot does not necessarily imply its sensitivity measures to be 0, due to the scale of the plots.

## Slide 17: Output Files
A Sensitivity_Plots.pdf file will be saved to ../SA_Output. Raw results from simulations are saved to ../SA_Simulations.

## Slide 18: Trouble Shooting
If error message says “in pull: undefined method ‘length’ for nil:NilClass” , first check whether uncertain parameters have been turned on correctly in the Parameter_UQ_Repository_V1.0.xlsx file (step 2).
If all the uncertain parameters have been turned on correctly, check whether the os model has corresponding uncertain parameters in the correct format that is supported by BCUS.